## Configuration
|  |  | Source A+Source B |  |  | % loading on each unit ( compared to Rated capacity of unit ) |  |  | Remark
s no | Type of Unit | Redundancy Configuration ( N+1, N+N etc ) | Total unit | Working | Standby | 100% IT load | 50% IT load | 25% IT load | Use the % loading of equipment calculated in this sheet to find ikW/TR from OEM curves. In case the OEM curves are not available, Signed declaration from OEM ( authorised person is required )
Chillers
DX based Package Unit ( PDx)
Primary Chilled Water Pumps
Secondary Chilled Water Pumps
Cooling Water Pumps
Dry Cooler/Adiabatic Cooling Tower/Cooling Tower
PAHU (Precision Air Handling Units)
Rear Door Coolers
Fan Wall Units
In-row Cooling Units (Chilled Water)
Other Cooling Units (including CDU for liquid cooling)
TFA Units
Comfort Cooling Units
PDUs (Power Distribution Units)
UPSs (Uninterruptible Power Supplies) - IT
UPSs (Uninterruptible Power Supplies) - Non-IT
Ventilation Fans
Transformers

## PUE
Sl no | PUE at varying IT load |  |  |  | Remarks
Annual
1 | IT Load | 100% | 50% | 25%
2 | IT Load, kW | 5000 | 2500 | 1250 | To be measured at rack PDU inlet
3 | IT Load,kW-HR | 43800000 | 21900000 | 10950000
4 | Running Hrs | 8760
5 | Cooling Infrastructure ikW/TR
6 | Total cooling load, TR | 0 | 0 | 0 | Based on cooling load calculation for the complete DC including all utilities like UPS rooms , Battery rooms, Electrical rooms, communication rooms, regularly occupied spaces etc. Submit Cooling Load Calculation
7 | Annuilized chiller ikW/TR | 0.6682 | 0 | 0 | Submit OEM data sheet showing annualised values or OEM Declaration, All values of GPM, Delta T , ambient conditions should be used as per actual design.
8 | Annuilized PDx ikW/TR ( for DX based cooling ) | 0 | 0 | 0 | Submit OEM data sheet showing annualised values or OEM Declaration, All values of GPM, Delta T , ambient conditions should be used as per actual design. Consider Power Consumption of Both Indoor and Outdoor unit.
9 | Primary Chilled water Pump power ikW/TR | 0 | 0 | 0 | OEM data sheet for power consumption for required GPM , convert to ikW/TR
10 | Secondary chilled water pump power ikW/TR | 0 | 0 | 0 | OEM data sheet for kW for required GPM , convert kW/GPM to ikW/TR
11 | Cooling water Pump power ikW/TR | 0 | 0 | 0 | OEM data ( applicable for water cooled unit & liquid cooling system)
12 | Dry cooler/ Adiabatic cooling tower /cooling tower ikW/TR | 0 | 0 | 0 | OEM data ( applicable for water cooled unit & Liquid cooling system)
15 | PAHU ikW/TR | 0 | 0 | 0 | OEM data showing fan curve efficiency at % loading ( from configuration sheet )
17 | Rear door ikW/TR | 0 | 0 | 0 | OEM data , Applicable only for active rear door.
19 | Fan wall units ikW/TR | 0 | 0 | 0 | OEM data showing fan curve efficiency at % loading ( from configuration sheet )
21 | Inrow cooling units( Chilled Water ), ikW/TR | 0 | 0 | 0 | Submit OEM data sheet showing annualised values or OEM Declaration, All values of Delta T , ambient conditions should be used as per actual design.
22 | Any other cooling unit ( including CDU for liquid cooling unit)
Regularly Occupied Area cooling
24 | TFA annuilized ikW/TR | 0 |  |  | OEM data, based on fresh air calculations
26 | Comfort annuilized ikW/TR | 0 |  |  | OEM data and comfort area cooling load calculation
27 | Cooling Infrastructure : Annuilized power consumption
Outdoor Units
28 | Chiller power consumption, kWHR | 0 | 0 | 0
29 | PDx power consumption, kWHR | 0 | 0 | 0
30 | Primary Chilled water pump power consumption, kWHR | 0 | 0 | 0
31 | Secondary Chilled water pump power consumption, kWHR | 0 | 0 | 0
32 | Condenser water pump power consumption, kWHR | 0 | 0 | 0
33 | Dry cooler/ Adiabatic cooling tower /cooling tower power consumption, kWHR | 0 | 0 | 0
34 | Indoor units
35 | PAHU, | 0 | 0 | 0
36 | Rear door | 0 | 0 | 0
37 | Fan wall units | 0 | 0 | 0
38 | Inrow cooling unit -Chilled water | 0 | 0 | 0
39 | Any other cooling unit | 0 | 0 | 0
40 | TFA | 0 | 0 | 0
41 | Comfort | 0 | 0 | 0
42 | Ventilation fan | 0 | 0 | 0
43 | Total HVAC Energy consumption | 0 | 0 | 0
44 | Electrical Losses
45 | PDU Losses | 0 | 0 | 0 | OEM data
46 | IT UPS loss | 0 | 0 | 0 | OEM data
47 | Non-IT UPS Loss | 0 | 0 | 0 | OEM data
48 | BMS Load | 0 |  |  | OEM data
49 | Lighting Load ( Exterior + Interior ) | 0 |  |  | OEM data
50 | Distribution losses | 0 | 0 | 0 | OEM data
51 | Transformer Losses | 0 | 0 | 0 | OEM data
52 | Total Electrical Losses + other support infra | 0 | 0 | 0
53 | Summary
54 | Total Facility Energy consumtion | 43800000 | 21900000 | 10950000
55 | PUE | 1 | 1 | 1
56 | Weightage | 0.2 | 0.35 | 0.45
57 | Weighted Average PUE for IGBC Credits |  |  | 1
Notes :-
PUE is based on facility all consuming electrical energy.
IT power shall be measured at rack PDU inlet.
In case UPS and battery is mounted in server racks , losses of same to be considered as part of non-IT loads
Battery loss is not considered as it shall be very low under float charging condition
The following areas shall be considered for comfort areas :- A) Reception & lobby areas dedicated to data centres. B) office areas dedicated to data centre buildings.