## Assess
IGBC Health and Well-being - Recertification Guideline
Project Checklist for Existing Buildings (Owner/ Tenant Occupied)
Pre-requisite: 1. Project must be occupied or in operation for at least 1 year. 2. Occupant Survey must be taken by atleast 70% of the building occupants ❖ Notes: 1. In case of expansion/ any new addition to existing facility, the project has to show the compliance for all Mandatory Requirements and Credits under IGBC Health and Well-being Rating System (Pilot Version)
2023-06-28
IGBC Health & Well-being Rating - Recertification Checklist
Modules |  | Points |  |  | Evidence |  | Remarks
|  | M | A | RE | Doc | Pic
Physical Well-being
Indoor Air Quality
IAQ MR1 | Tobacco Smoke Control | Required | Y |  | Not Required
IAQ MR2 | Fresh Air Ventilation | Required | Y |  |  1. Report indicating the ambient air quality within the site 2. Submit the Operation & Maintenance Plan for the fresh air ventilation system 3. Test reports of the fresh air ventilation systems in operation | 1. Photographs of typical fresh air inlet, vents and exhaust as applicable.
IAQ Credit 1 | Monitor Indoor Air Quality | 7 | 4 | 3 | 1. Air Quality data in the preceeding 3 years. 2. Air quality report with the details of daily and quarterly monitored parameters 3. Details of measures adopted to improve indoor air quality 4. Display of IAQ parameters in common areas 5. Operation & Maintenance Plan for the IAQ monitoring and Control systems | 1. Photograph of display of monitored parameters 2. Photograph of display unit in common area
IAQ Credit 2 | Reduce Indoor emissions | 3 | 1 | 2 | 1. Test reports from the preceeding 3 years. 2. Microbial Count Test report (Air sample + Swab sample). 3. Details of measures adopted to reduce indoor emissions and microbes.
|  | 10 | 5 | 5
Water Quality
WQ MR1 | Access to Drinking Water | Required | Y |  | Not Required
WQ Credit 1 | Quality of Drinking Water | 3 | 3 | 0 | 1. Last 3 years test reports of Potable water (Drinking + Domestic)
WQ Credit 2 | Quality of Recycled Water | 3 | 3 | 0 | 1. Last 3 years test reports for the recycled water quality
|  | 6 | 6 | 0
Comfort
CT MR1 | Occupant Satisfaction Survey | Required | Y |  | Last 3 years report indicating the details of survey conducted and its results (min 70% satisfaction levels. For comfort credits point - 1. Occupant comfort survey report for the preceding one year (Min 80% satisfaction for credit points)
CT Credit 1 | Visual Comfort | 11 | 6 | 5 | No required.
CT Credit 2 | Thermal Comfort | 6 | 4 | 2 | 1. Indoor temperature, RH & Air velocity readings during summer, monsoon and winter. The percentage of operating hours the parameters are maintained
CT Credit 3 | Acoustic Comfort | 6 | 4 | 2 | 1. Last 1 year detailed acoustical survey report highlighting the levels of Noise Isolation Class, Noise Criterion and Reverberation Time in the regularly occupied spaces.
CT Credit 4 | Olfactory Comfort | 4 |  | 4 | Not Required
CT Credit 5 | Ergonomics | 4 |  | 4 | Not Required
CT Credit 6 | Comfort for Differently Abled Occupants | 4 |  | 4 | Not Required
|  | 35 | 14 | 21
Health & Sanitation
HS Credit 1 | Housekeeping | 2 | 2 |  | 1. Housekeeping report for last 3 years. 2. Pest management report for last 3 years
HS Credit 2 | Eco-friendly Chemicals | 1 | 2 |  | 1. Details of housekeeping chemicals used and their applications in the last 3 years 2. Purchase invoices of eco-friendly housekeeping chemicals procured in the last 3 year | Photographs of House keeping Chemicals purchased
HS Credit 3 | Control of Outdoor Dust Pollutants | 1 |  | 1 | Not Required
|  | 4 | 4 | 1 | 
Fitness & Nutritional Choices
FNC Credit 1 | Fitness Facilities | 4 | 0 | 4 | Not Required
FNC Credit 2 | Awareness on Physical Fitness | 3 | 3 |  | Awareness 1. Report on various measures taken in last 3 years for creating awareness with supporting photographs 2. Copies of circulars and emails Encouragement 1. Report on various initiatives taken in the last 3 years for encouraging the occupants to adopt fitness practices. 2. Details of Health/Medical camps conducted in the last 3 years | 1. Enclose supporting photographs where applicable.
FNC Credit 3 | Nutritional Choices | 3 | 3 |  | Details of nutritional food choices adopted in the last 3 years | 1. Photographs of display of nutritional facts
|  | 10 | 6 | 4
Emotional and Intellectual Well-being
E&IW Credit 1 | Exterior Connectivity to Occupants | 12 | 6 | 6 | Not Required
E&IW Credit 2 | HR Policies | 6 | 6 | 0 | Not Required
E&IW Credit 3 | Spiritual Well-being | 2 | 2 | 0 | Not Required
|  | 20 | 14 | 6
Social Well-being
SW Credit 1 | Recreation and Culture | 4 | 4 | 0 | 1. Details of National/ Cultural festivals celebrated in the last 3 years, within the facility and recreational & leisure activities organised. | Supporting photographs of recreational and cultural activities.
SW Credit 2 | Employee safety | 5 | 5 | 0 | Not Required
SW Credit 3 | Service to Society | 1 | 1 | 0 | 1. Details of the initiatives taken in the last 3 years along with the supporting documents and photographs
|  | 10 | 10 | 0
Innovation & Design
ID Credit 1 | Innovation & Design | 1 | 0 | 1
ID Credit 2 | Innovation & Design | 1 | 0 | 1
ID Credit 3 | Innovation & Design | 1 | 0 | 1
ID Credit 4 | Innovation & Design | 1 | 0 | 1
ID Credit 5 | Innovation & Design | 1 | 1
|  | 5 | 1 | 4
Total |  | 100 | 60 | 41
Certification Level | Recognition | Credits
Certified | Best Practices | 50-59
Silver | Outstanding Performance | 60-69
Gold | National Excellence | 70-79
Platinum | Global Leadership | 80-100

## Parameter
Wellbeing Parameters (Macro Level) |  | 5 Senses
|  | Smell | Taste | Sight | Touch | Sound
| Indoor Air Quality | CRD/ CNR |  | VHI
PHYSICAL WELL-BEING | Water Quality |  | CNR
| Thermal Comfort |  |  |  | CVD
| Visual Comfort |  |  | VHI |  | VHI
Acoustic Comfort
| Olfactory Comfort | CRD
| Ergonomics |  |  |  | BJD
| Nutrition Enhancement |  | CVD/ CNR/ DBS
| Health & Sanitation | CRD
Wellbeing Parameters (Macro Level) |  | 5 Senses
|  | Smell | Taste | Sight | Touch | Sound
EMOTIONAL & INTELLEC- TUAL WELL-BEING | Recreational & Cultural | CRD |  |  | CVD/DBS
Greenery- Interior & exterior
| Connectivity with Nature |  |  | VHI
| Employee Friendly Environment | CVD / DBS
| Bonding with employees | CVD / DBS
| Spiritual wellbeing | CVD / DBS
Wellbeing Parameters (Macro Level) |  | 5 Senses
|  | Smell | Taste | Sight | Touch | Sound
| Community engagement | CVD / DBS
| Safety & Security | CVD / DBS
| Element | Consciousness | Organ | Perception
| Earth | Olfactive | Nostrils | Smell
| Water | Gustative | Tongue | Taste
| Fire | Visual | Eyes | Form
| Air | Tactual | Skin | Touch
| Ether | Auditive | Ears | Sound

## IAQ
Minimum Ventilation Rates in Breathing Zone
Occupancy Category | People Outdoor Air rate (Rp) |  | Area Outdoor Air Rate, (Ra)
| Cfm / Person | 1 / s Person | Cfm / fl2 | 1 / s.m2
Office Building
Office Space | 5 | 2.5 | 0.06 | 0.3
Reception areas | 5 | 2.5 | 0.06 | 0.3
Main entry lobbies | 5 | 2.5 | 0.06 | 0.3
Parameters | Threshold values |  |  | Frequency of Monitoring
| Class A | Class B | Class C
CO2 | Max 350 ppm above ambient | Max 440 ppm above ambient | Max 530 ppm above ambient
PM 2.5 | < 15 µg/m³ | < 20 µg/m³ | < 25 µg/m³
PM 10 | < 50 µg/m³ | < 75 µg/m³ | < 100 µg/m³ | Daily Monitoring
CO | < 2 ppm | < 6 ppm | < 9 ppm
O3 | < 50 µg/m³ | <75 µg/m³ | <100 µg/m³
TVOC *
(equivalent to isobutylene) | < 500 µg/m³ | < 650 µg/m³ | < 800 µg/m³ | Quarterly Monitoring
SO2 | < 40 µg/m³ | < 80 µg/m³ | -
NO2 | < 40 µg/m³ | < 80 µg/m³ | -
| 6 | 3 | 1
Parameters | Threshold values Class A | Threshold values Class B | Frequency of Monitoring
Indoor Emissions & Microbial Count
CH2O | < 30 µg/m³ | < 100 µg/m³ | Quarterly Monitoring
Total Microbial Count | 50 CFU/ m³ | 150 CFU/ m³
| 3 | 1 | 0

## Water
Characteristic | Requirement (Acceptable Limit)
Physical Parameters
Colour, Hazen units | 5
Odour | Nil
pH value | 6.5 - 8.5
Turbidity, NTU | 1
Total dissolved solids, mg/l | 500
General Parameters
Total Hardness CaCO3, mg/l | 200
Total alkalinity as calcium carbonate, mg/l, Max | 200
Calcium (as Ca), mg/l | 75
Magnesium as Mg, mg/l | 30
Chloride as Cl, mg/l | 250
Sulphate as SO4, mg/l | 200
Iron as Fe, mg/l | 0.3
Toxic Parameters
Lead | 0.01
Mercury | 0.001
Cadmium | 0.003
Total Chromium | 0.05
Total Arsenic | 0.01
Pesticide | Annexure-IV
Bacteriological Parameter
E. coli | Shall not be detectable in any 100 ml sample
Recycled Water as per CPCB-2015
Parameters | Threshold limits
pH | 6.5-9
BOD (mg/l) | Not more than 10
COD (mg/l) | Not more than 50
TSS (mg/l) | Not more than 20
NH4N (mg/l) | Not more than 5
N-total (mg/l) | Not more than 10
Fecal Coli form (MPN/100 ml) | Not more than 100
Characteristic | Requirement (Acceptable Limit)
Physical Parameters as per IS 10500: 2012
Colour, Hazen units | 5
Odour | Nil
Turbidity, NTU | 1
Total dissolved solids, mg/l | 500

## comfort
Percentage of regularly occupied areas | Points
50% | 1
60% | 2
70% | 3
Type of spaces | Limiting Glare Index
General offices | 19
Deep plan general offices | -
Computer workstation | -
Conference room | 19
Executive offices | 19
Business machine operation | 19
Lobbies, Waiting rooms | -
Rest rooms | -
Interior parking areas | -
Occupied Spaces | The percentage of satisfied occupants
| Class A | Class B | Class C
General Office space, Conference room, Workstations, Cafeteria/Restaurant, Common areas, Reception
| 90% | 85% | 80%
Type of Building/Space | Temperature (°C) |  | Humidity | Air Velocity
| Summer | Winter
General Office space, Conference room, Workstations, Cafeteria/ Restaurant, Common areas, Reception
| 24.5 + 2.5 | 22.0 + 3.0 | 30 % – 70 % | < 0.2 m/s
Percentage of operating hours | Points
75% | 1
85% | 2
95% | 3
Space | Class B
Executive & private offices | 35
Conference Rooms | 35
Teleconference rooms | 25 max
Open- plan office spaces | 40
Corridors & lobbies | 45
Space | Reverberation Time (Sec)
Open Office Plan | <1.0
Meeting Rooms | < 0.8
Video Conference Rooms | <0.6
Collaborative spaces | <1.25
Private cabins | <1.0

## E&I
Percentage of total area with green cover | Points
> 15% | 1
> 20% | 2
> 25% | 3
> 30% | 4
> 35% | 5
Percentage of regularly occupied spaces with connectivity to the outdoors | Points
> 25% | 1
> 35% | 2
> 45% | 3
> 55% | 4
> 65% | 5

## Annex
Annexure
Annexure-I | Minimum Ventilation Rates in Breathing Zone
Annexure-II | Measurement Methodology of Indoor Air Quality Parameters
Annexure-III | Specifications of the Instrument to be used for Measuring IEQ Parameters
Annexure-IV | Pesticide Residues Limits and Test Method
Annexure-V | Required Air Speed to Offset Increased Temperature
Annexure-VI | Measurement Methodology for Thermal Comfort
Annexure-VII | Reverberation Time
Annexure-VIII | Measurement Methodology for Acoustic Comfort